## Slide 1: Intelligent Controllers for Load Frequency Control of a Two-Area Power System
S. A. Azeer
R. Ramjug-Ballgobin
S. Z. Sayed Hassen

## Slide 2: Outline of Talk
Frequency Regulation
Power System Modelling
  Non-Reheat steam turbine
  Reheat steam turbine
  Hydraulic turbine
Compensator Design
  PID controller
  Fuzzy logic controller
  ANN controller
Simulation of Compensated Systems
Conclusion

## Slide 3: Frequency Regulation
The mismatch between the generating capacity of a power system and the load demand at any given moment in time is reflected in the system’s frequency.
Large deviations from a chosen nominal value of frequency are undesirable.
Power system’s frequency is traditionally regulated using proportional-integral-derivative (PID) controllers.
Frequency is dependent on real power generated.
When real power generated > load demand, frequency increases and vice versa.
The primary control action is performed by the governor (range of seconds)
The secondary control action is performed by the LFC (range of minutes)

## Slide 4: Frequency Regulation
Another parameter of interest when dealing with more than area system is the Area Control Error (ACE).
It is a measure of power that is obtained from other area(s) when/after a disturbance has occurred.
A basic guiding principle in power system is that each area must absorb its own load under steady state conditions.
A constant ACE will imply that one area will have to support the other on a steady-state basis.
=
=

## Slide 5: Aims
To perform a comparative analysis of three different compensators on systems operating with different turbines.
Design suitable compensators to provide the secondary control actions to the systems based on the following criteria:
  Steady-state error for frequency and Area Control Error
  Deviation from nominal frequency
  Settling time

## Slide 6: Power System Modelling
Two types of Power Systems:
  Hydro
  Thermal
Three types of turbines available:
  Hydro Power System Hydraulic turbine
  Thermal Power System Reheat and Non-Reheat turbine

## Slide 7: Turbine Modelling
Non-Reheat Steam Turbine
=
  is the delay between the change in the valve opening position and the mechanical torque of the turbine.
Reheat Steam Turbine
is the time constant of the reheater
is the rating of the high pressure stage with respect to total generated mechanical power of turbine.
Hydraulic Turbine
=

## Slide 8: Two Area Power System Model

## Slide 9: Compensator Design
The three chosen compensators are:
PID
Fuzzy Logic
NARMA-L2
The PID controller was chosen for a proper comparative analysis to be carried out between a conventional controller and intelligent ones

## Slide 10: PID Controller
PID controller is the extreme form of a lead-lag compensator
and are the gains of the Proportional, Integral and Derivative terms of the PID
Tuning of parameters by self tuning algorithm in MATLAB

## Slide 11: Fuzzy Logic Controller
K1, K2 and K3 are the scale factors of controller
Stages of Fuzzy Logic Controller design:
  Fuzzification
  Rule base set up
  Decision-making stage
  Deffuzification

## Slide 12: Fuzzy Logic Fuzzification and Rule-base Set-Up
Rule-base Set-Up
M: Large Negative P: Small Positive
N: Small Negative Q: Large Positive
O: Zero

## Slide 13: Fuzzy Logic Decision-Making and Defuzzification
Execution of rules according to Rule Table to obtain a Fuzzy control output from the Inference System
Rule Table was taken from previous research on LFC
Defuzzification consists of producing a non-Fuzzy control action from the Inference System that will rectify the ACE output
Method used: centroid

## Slide 14: ANN-NARMA-L2 Architecture
Nonlinear Autoregressive Moving Average (NARMA-L2)
ACE output y should follow the reference model output yr to completely eliminate error in the system
Controller should provide control input u to adjust ACE output y by finding the ratio of two previously determined functions.
Design consists of two stages:
  Plant Identification
  Control Design

## Slide 15: ANN-NARMA-L2 Plant Identification
Training of ANN such that it is representative of the actual dynamics of the plant
The parameters of the Network architecture were chosen from previous published papers
Training data was obtained by importing the input and output data of the PID into the network
Training function chosen was the Levenberg-Marquardt back-propagation algorithm

## Slide 16: ANN-NARMA-L2 Control Design
The reference model must be zero such that the plant ACE output y follows the reference model output yr and becomes zero
A constant set to ‘0’ is inserted at the reference input of the controller

## Slide 17: Hydro-Non Reheat Thermal Power System
Frequency deviation
ACE Output

## Slide 18: Hydro-Reheat Thermal Power System
Frequency deviation
ACE Output

## Slide 19: Non Reheat-Reheat Thermal Power System
Frequency deviation
ACE Output

## Slide 20: Conclusion and Further Works
Percentage frequency overshoot and undershoot have been reduced considerably for the Intelligent controllers c.f. PID controller
The ACE outputs however got worse but ultimately goes to zero !!!
To improve response of systems:
  Design of Fuzzy-PID to eliminate errors due to variable load-change
  Adaptive membership functions plots of the Fuzzy Logic and adaptive inputs to NARMA-L2 to match variable load-change
Validate results on areas with two or more generating units and with more interconnected areas.

## Slide 21: Thank You…